## Metal & IPS PVC Pipes
METAL & IMPERIAL PVC PIPE DIMENSIONS
Reference Standards: ASME B36.10M / B36.19M (Steel) & ASTM D1785 (Schedule 40/80 PVC)
NPS (inches) | DN (metric equivalent) | Outside Diameter (mm) | Outside Diameter (inches) | Standard Reference Sizing
1/8" | DN 6 | 10.3 | 0.405 | ASME B36.10M / ASTM D1785
1/4" | DN 8 | 13.7 | 0.54 | ASME B36.10M / ASTM D1785
3/8" | DN 10 | 17.1 | 0.675 | ASME B36.10M / ASTM D1785
1/2" | DN 15 | 21.3 | 0.84 | ASME B36.10M / ASTM D1785
3/4" | DN 20 | 26.7 | 1.05 | ASME B36.10M / ASTM D1785
1" | DN 25 | 33.4 | 1.315 | ASME B36.10M / ASTM D1785
1-1/4" | DN 32 | 42.2 | 1.66 | ASME B36.10M / ASTM D1785
1-1/2" | DN 40 | 48.3 | 1.9 | ASME B36.10M / ASTM D1785
2" | DN 50 | 60.3 | 2.375 | ASME B36.10M / ASTM D1785
2-1/2" | DN 65 | 73 | 2.875 | ASME B36.10M / ASTM D1785
3" | DN 80 | 88.9 | 3.5 | ASME B36.10M / ASTM D1785
3-1/2" | DN 90 | 101.6 | 4 | ASME B36.10M / ASTM D1785
4" | DN 100 | 114.3 | 4.5 | ASME B36.10M / ASTM D1785
5" | DN 125 | 141.3 | 5.563 | ASME B36.10M / ASTM D1785
6" | DN 150 | 168.3 | 6.625 | ASME B36.10M / ASTM D1785
8" | DN 200 | 219.1 | 8.625 | ASME B36.10M / ASTM D1785
10" | DN 250 | 273 | 10.75 | ASME B36.10M / ASTM D1785
12" | DN 300 | 323.9 | 12.75 | ASME B36.10M / ASTM D1785
14" | DN 350 | 355.6 | 14 | ASME B36.10M / ASTM D1785
16" | DN 400 | 406.4 | 16 | ASME B36.10M / ASTM D1785
18" | DN 450 | 457.2 | 18 | ASME B36.10M / ASTM D1785
20" | DN 500 | 508 | 20 | ASME B36.10M / ASTM D1785
24" | DN 600 | 609.6 | 24 | ASME B36.10M / ASTM D1785

## Metric PVC Pipes
METRIC PVC PRESSURE PIPE DIMENSIONS
Reference Standards: EN ISO 1452 / DIN 8062 (Sized directly by Outside Diameter)
Nominal Size (DN/OD) | Outside Diameter (mm) | Outside Diameter (inches) | Approx. NPS Equivalent | Standard Reference Sizing
d_n 12 mm | 12 |  | 1/4" | EN ISO 1452 / DIN 8062
d_n 16 mm | 16 |  | 3/8" | EN ISO 1452 / DIN 8062
d_n 20 mm | 20 |  | 1/2" | EN ISO 1452 / DIN 8062
d_n 25 mm | 25 |  | 3/4" | EN ISO 1452 / DIN 8062
d_n 32 mm | 32 |  | 1" | EN ISO 1452 / DIN 8062
d_n 40 mm | 40 |  | 1-1/4" | EN ISO 1452 / DIN 8062
d_n 50 mm | 50 |  | 1-1/2" | EN ISO 1452 / DIN 8062
d_n 63 mm | 63 |  | 2" | EN ISO 1452 / DIN 8062
d_n 75 mm | 75 |  | 2-1/2" | EN ISO 1452 / DIN 8062
d_n 90 mm | 90 |  | 3" | EN ISO 1452 / DIN 8062
d_n 110 mm | 110 |  | 4" | EN ISO 1452 / DIN 8062
d_n 125 mm | 125 |  | 4-1/2" | EN ISO 1452 / DIN 8062
d_n 140 mm | 140 |  | 5" | EN ISO 1452 / DIN 8062
d_n 160 mm | 160 |  | 6" | EN ISO 1452 / DIN 8062
d_n 200 mm | 200 |  | 8" | EN ISO 1452 / DIN 8062
d_n 225 mm | 225 |  | 8" (Oversize) | EN ISO 1452 / DIN 8062
d_n 250 mm | 250 |  | 10" | EN ISO 1452 / DIN 8062
d_n 280 mm | 280 |  | 10" (Oversize) | EN ISO 1452 / DIN 8062
d_n 315 mm | 315 |  | 12" | EN ISO 1452 / DIN 8062
d_n 355 mm | 355 |  | 14" | EN ISO 1452 / DIN 8062
d_n 400 mm | 400 |  | 16" | EN ISO 1452 / DIN 8062
d_n 450 mm | 450 |  | 18" | EN ISO 1452 / DIN 8062
d_n 500 mm | 500 |  | 20" | EN ISO 1452 / DIN 8062
d_n 630 mm | 630 |  | 24" | EN ISO 1452 / DIN 8062

## Side-by-Side Comparison
METAL (IPS) VS. METRIC PVC SIDE-BY-SIDE COMPARISON
Crucial for sizing transition joints. Steel and Metric PVC Outside Diameters (OD) DO NOT match.
Nominal Group | Metal / IPS OD (mm) | Metal / IPS OD (in) | Metric PVC OD (mm) | Metric PVC OD (in) | OD Diff (mm) | OD Diff (in) | Compatibility & Sizing Notes
1/4" / DN 8 | 13.7 | 0.54 | 12 |  |  |  | Requires transition adapter. Sizes differ by 1.7 mm.
3/8" / DN 10 | 17.1 | 0.675 | 16 |  |  |  | Requires transition adapter. Sizes differ by 1.1 mm.
1/2" / DN 15 | 21.3 | 0.84 | 20 |  |  |  | Requires transition adapter. Common conversion size.
3/4" / DN 20 | 26.7 | 1.05 | 25 |  |  |  | Requires transition adapter. Common conversion size.
1" / DN 25 | 33.4 | 1.315 | 32 |  |  |  | Requires transition adapter. Sizes differ by 1.4 mm.
1-1/4" / DN 32 | 42.2 | 1.66 | 40 |  |  |  | Requires transition adapter. Sizes differ by 2.2 mm.
1-1/2" / DN 40 | 48.3 | 1.9 | 50 |  |  |  | Requires transition adapter. Metric OD is larger by 1.7 mm.
2" / DN 50 | 60.3 | 2.375 | 63 |  |  |  | Very common sizing mismatch! Metric OD is 2.7 mm larger. Adapt via threads/flanges.
2-1/2" / DN 65 | 73 | 2.875 | 75 |  |  |  | Requires transition adapter. Metric OD is 2.0 mm larger.
3" / DN 80 | 88.9 | 3.5 | 90 |  |  |  | Requires transition adapter. Metric OD is 1.1 mm larger.
4" / DN 100 | 114.3 | 4.5 | 110 |  |  |  | Significant mismatch! Metal is 4.3 mm larger. Transition fittings are mandatory.
5" / DN 125 | 141.3 | 5.563 | 140 |  |  |  | Requires transition adapter. Metal OD is 1.3 mm larger.
6" / DN 150 | 168.3 | 6.625 | 160 |  |  |  | Significant mismatch! Metal is 8.3 mm larger. Transition fittings are mandatory.
8" / DN 200 | 219.1 | 8.625 | 200 |  |  |  | Very large mismatch (19.1 mm). Note: Metric PVC also has OD 225 mm which is closer to metal OD.
8" (Alt) / DN 200 | 219.1 | 8.625 | 225 |  |  |  | Metric OD 225 is 5.9 mm larger than Metal OD 219.1.
10" / DN 250 | 273 | 10.75 | 250 |  |  |  | Large mismatch (23.0 mm). Note: Metric PVC also has OD 280 mm which is closer.
10" (Alt) / DN 250 | 273 | 10.75 | 280 |  |  |  | Metric OD 280 is 7.0 mm larger than Metal OD 273.0.
12" / DN 300 | 323.9 | 12.75 | 315 |  |  |  | Mismatch of 8.9 mm. Requires specific transition flanges.
14" / DN 350 | 355.6 | 14 | 355 |  |  |  | Extremely close! Only 0.6 mm difference, but still requires material-specific joints.
16" / DN 400 | 406.4 | 16 | 400 |  |  |  | Mismatch of 6.4 mm. Transition flanges/couplings required.
18" / DN 450 | 457.2 | 18 | 450 |  |  |  | Mismatch of 7.2 mm. Transition fittings required.
20" / DN 500 | 508 | 20 | 500 |  |  |  | Mismatch of 8.0 mm. Transition fittings required.
24" / DN 600 | 609.6 | 24 | 630 |  |  |  | Large mismatch (20.4 mm). Metric OD is larger.